## Slide 1
PPA JUMPER AUDIT WEEK-40
Process Plant Area | Week 40 · 2026 | Period: W40 (2026)
DRYER–CM
4 jumpers
KILN–CTS
3 jumpers
FURNACE
0 jumpers
CONVERTER
0 jumpers
Total Jumper with Authorized/MoC
3
Total Removed (W40, 2026)
0
Jumper Update Table
PLC | Update Jumper | Installed | Authorized | Due Date
D3C | Shortbranches installed on PLC D3C, FSL (Flow Switch Low) Feed conv. Dryer 3 | Wk10 2026 | ✓ | Wk51 2026
D3C1 | Shortbranches installed on PLC D3C MainFlame On Interlock to TR ESP | wk16 | ✓ | Perlu konfirmasi
CMS1 | Forces installed on PLC CMS1 Level HiHi Switch Surge Bin - Digital_Alarms | Re-installed wk27 | ✓ | Wk27 2026
K2C | Conveying Blower opr ready E4AM01 on PLC K2C | Wk39 2026 | — | Perlu konfirmasi
K2C | Conveying Blower opr ready H21M03 on PLC K2C | Wk39 2026 | — | Perlu konfirmasi
K2C | Conveying Blower opr ready H21M04 on PLC K2C | Wk39 2026 | — | Perlu konfirmasi
Remaining Jumper List (3)
No | ID | PLC | Description
1 | J-004 | K2C | Conveying Blower opr ready E4AM01 on PLC K2C
2 | J-005 | K2C | Conveying Blower opr ready H21M03 on PLC K2C
3 | J-006 | K2C | Conveying Blower opr ready H21M04 on PLC K2C
Remaining PLC Ratio
4 / 69 (5.8%)
PLC with active jumpers / Total PLC in Scope
Count of Remaining Jumper on PLC PP Area
Chart: 
| CMS1 | D3C | D3C1 | K2C
AFI | 0 | 0 | 0 | 3
Shortbranches | 0 | 1 | 1 | 0
Forces | 1 | 0 | 0 | 0